NIT No. CPDL/FY25-26/HT & LT Cable/008

Open Tender Notification

FOR

02 Years Rate Contract for the Supply of HT and LT Cables in Chandigarh, CPDL.

Tender Enquiry No.: CPDL/FY25-26/HT & LT Cable/008 Dated 08th July 2025

Due Date for Bid Submission: 29.07.2025

(Up to 17:00 Hrs)

Chandigarh Power Distribution Limited

SCO 33-35, 4th Floor, Sector 34-A

Chandigarh - 160022, India

Website: www.chandigarhpower.com

TABLE OF CONTENTS

| SECTION NO. | DESCRIPTION |
| --- | --- |
| SECTION - I | Request for Quotation with calendar of events |
| SECTION - II | Instructions for Bidders (IFB) |
| SECTION - III | Special Terms & Conditions of Contract (SCC) |
| SECTION - IV | General Conditions of Contract (GCC) |
| SECTION - V | Price Bid format |
| SECTION - VI | General Format (Appendix) |
| SECTION - VII | Technical Specifications |

SECTION – I: REQUEST FOR QUOTATION

INVITATION FOR BIDS

CPDL hereby invites bids for 02 Years Rate Contract for the supply of HT and LT Cables as per the detailed technical specifications provided in the bid document.

Prospective bidders are encouraged to manufacture the HT and LT Cables within India, aligning with the 'Make in India' initiative, to foster local industry growth, reduce delivery times, and ensure more efficient after-sales support.

Bidders are required to abide by all relevant environmental and safety regulations in India and to outline their waste, noise, and oil leak management measures.

- Event Information:

Chandigarh Power Distribution Limited (“CPDL”) invites bids for HT and LT Cables as per the Technical Specification as stipulated elsewhere in this tender document. BoQ is as below:

| Sl No | Voltage Level | Item Description | Qty | UoM | EMD (in Lakhs) |
| --- | --- | --- | --- | --- | --- |
| 1 | HT | 11kV 3C X 300 Sq mm | 111000 | Mtr | 40.00 |
| 2 |  | 11kV 3C X 70 Sq mm | 3000 | Mtr |  |
| 3 | LT | 1.1 kV 4C X 150 Sq mm | 8000 | Mtr |  |
| 4 |  | 1.1 kV 4C X 95 Sq mm | 198000 | Mtr |  |
| 5 |  | 1.1 kV 4C X 400 Sq mm | 27000 | Mtr |  |
| 6 |  | 1.1 kV 2C X 10sqmm | 100000 | Mtr |  |
| 7 |  | 1.1 kV 4C X 16sqmm | 100000 | Mtr |  |
| 8 |  | 1.1 kV 4C X 35sqmm | 60000 | Mtr |  |
| 9 |  | 1.1 kV 4C X 50sqmm | 60000 | Mtr |  |

  - The schedule of specifications with detailed terms & conditions can be obtained from the CPDL tender website www.chandigarhpower.com against submission of tender fee (non-refundable) via online transfer mode (NEFT/RTGS) only of Rs.1180/- “(Inclusive of GST)”. (No Other mode of tender fee will be acceptable)

CPDL Bank Details for transferring Tender Fee is as below:

Account Name                  : Current Account

Bank Name                       : State Bank of India

Bank Account No             : 43632537888

IFSC Code                       : SBIN0000628

In case tender papers are downloaded from the above website, then the bidder has to enclose the scan copy of money receipt/UTR No (proof of online transfer) against submission of tender fee during submission of Bid document.

1.02 Calendar of Events:

Bids must be submitted within the stipulated “DATE & TIME IN HRS” as mentioned in the event calendar.

| Sl No | Event Details | Date & Time |
| --- | --- | --- |
| (A) | Sale/ availability of tender documents from Website | 08.07.2025, 17:00 Hrs |
| (B) | Receipt of pre-bid queries, if any | 15.07.2025, 17:00 Hrs |
| (C) | Posting Consolidated response to all the pre-bid queries as received | 22.07.2025, 17:00 Hrs |
| (D) | Last date and time of receipt of Bids | 29.07.2025, 17:00 Hrs |

1.03 Chandigarh Power Distribution Limited reserves the right to accept / reject any or all Tenders without assigning any reason thereof in the event of following:

(i) Non-Submission of Tender Fee.

(ii) Earnest Money Deposit (EMD) is not deposited in shape of Bank Guarantee/Online Transfer.

(iii) The offer does not contain prices indicating break-up towards all taxes & duties in prescribed format.

(iv) Complete Technical details are not enclosed.

(v) Tender is received after due date and time.

(vi) Technical offer contains any prices.

2.0 Qualification Criteria: -

Technical Qualification Criteria:

Approved Makes: KEI/UCL/Torrent/Havells/Gemscab/Laser Power

Financial Qualification Criteria:

1. OEM must have an Average Annual Sales Turnover of Rs 500 Crores, considering the best three financial years out of the last four, i.e., FY2021-22, FY2022-23, FY2023-24, and FY2024-25. Audited Financial Statements / CA Certificate to be submitted in this regard.

2. Or if the bidder is an Authorized Channel Partner, they must have an Average Annual Sales Turnover of Rs 15 Crores, considering the best three financial years out of FY2021-22, FY2022-23, FY2023-24, and FY2024-25. Audited Financial Statements / CA Certificate to be submitted in this regard.

2. Bidder must submit an undertaking confirming that they have not been blacklisted or debarred by any Central or State Government department, Electricity Utility, or PSU.

3. Bidder must submit an undertaking confirming that no proceedings are pending against them under the Insolvency and Bankruptcy Code, 2016 (IBC).

4. Bidder must submit an undertaking stating that no litigation is pending with CPDL or its group/associate companies.

5. The bidder must have a valid PAN No., GST Registration Number, in addition to other statutory compliances. The bidder must submit an undertaking that the bidder shall comply with all the statuary compliances as per the laws/rules etc. before the start of the supply/work. In case of MSME bidder, the bidder must submit a copy of MSME Certificate.

3.00 Bidding and Award Process

Bidders are requested to submit their offer in line with this Tender document.

All future correspondence regarding the tender, bid submission, bid submission date extension, Pre-bid query etc. shall be through CPDL tender website.

3.01 Bid Submission

- Technical Bid & Price Bid shall be submitted over email to tender.cpdl@rpsg.in.

- Please ensure that the price bid is submitted as a password-protected file. Submitting the price bid without password protection may lead to rejection of your bid.

- Password to be submitted on request from CPDL to the separate mail ID as per the instruction.

The bidders are required to submit the bids in 3 (three) parts.

# 3.01.1: First Part: EMD

A. EMD as applicable shall be submitted in the form of Bank Guarantee or online transfer (NEFT/ RTGS). The EMD shall be valid for 120 days from the due date of bid submission. The EMD BG has to be strictly in the format as mentioned in General Condition of Contract, failing which it shall not be accepted by CPDL and the bid as submitted shall be liable for rejection.

B. A separate non-refundable tender fee of stipulated amount also needs to be transferred online through NEFT/ RTGS in case the tender document is downloaded from our website/in any mode of receipt of tender document.

CPDL Bank Details for transferring Tender Fee and EMD is as below:

Account Name                : Current Account

Bank Name                     : State Bank of India

Bank Account No           : 43632537888

IFSC Code                     : SBIN0000628

3.01.2: Second Part: Technical Bid

Techno-Commercial bid shall contain the following documents. Absence of any of these may attract bid rejection:

- Index Stating Document name & Page No./Document No. in bid. As illustrated below:

| Sr No | Document | Page No/Document No |
| --- | --- | --- |
| 1 | Type test Reports | 3 |
| 2 | Schedule of Deviations | 8 |
| 3 | … | … |

- Requisite Documents for compliance to Qualification Criteria

- Scan Copy of Tender Fee and EMD

- Duly Signed and stamped copy of complete bid document, amendment/Corrigendum if any, Technical Specifications, etc.

- Duly Signed and Stamped copy of filled annexures/form/appendix, which is to be submitted as per the bid document.

- Type Test Certificate of same or higher rating.

- Duly signed and stamped ‘No Deviation Certificate’ as per Enclosed Annexure on bidder’s letter head.

- Proper authorization letter / Power of Attorney to sign the tender on the behalf of bidder.

- Copy of PAN, GST registration (In case any of these documents is not available with the bidder, same to be explicitly mentioned in the ‘Schedule of Deviations’)

3.01.3:  Third Part: Price Bid

Price Bid shall contain only the price details and strictly in format as mentioned in Annexure I along with explicit break up of basic prices and Taxes & duties etc. In case any discrepancy is observed between the item description stated in Schedule of Items mentioned in the tender and the price bid submitted by the bidder, the item description as mentioned in the tender document (to the extent modified through Corrigendum issued if any) shall prevail. The price bids containing any deviations/conditions shall be liable to be rejected.

“Price Bid must be submitted in password protected file, and will be opened after techno-commercial evaluation and only of the qualified bidders. Password of price bid shall be asked from qualified bidders through separate email after technical evaluation.”

The Bid prepared by the Bidder, and all correspondence and documents relating to the Bid exchanged by the Bidder and CPDL, shall be written in the English Language. Any printed literature furnished by the Bidder may be written in another Language, provided that this literature is accompanied by an English translation, in which case, for purposes of interpretation of the Bid, the English translation shall govern.

Bidder must ensure that Technical Bid should not contain any cost information whatsoever and shall be submitted within the due date.

Please follow below instruction for submitting bid at our email tender.cpdl@rpsg.in.

- One folder should contain scan copy of bank transfer proof/documents of EMD & Tender fee, in case bidder wish to submit EMD as bank Guarantee, scan copy of BG should be uploaded in the folder, Original copy of EMD BG must be submitted on or before bid submission date at our below address, NIT No. and Tender description should be mentioned on the envelope.

Manager (C&MM)

Chandigarh Power Distribution Limited

SCO 33-35, 4th Floor, Sector 34-A

Chandigarh - 160022, India

- Second folder should contain complete set of techno-commercial bid documents.

- Third folder should contain only Price bid and price bid must be in password protected file.

All above folders should be in one folder and name of folder should our NIT No./Tender description.

3.02 Reverse Auction: Purchaser reserves the right to use Reverse Auction as an optional tool as an integral part of the entire tendering process. All techno-commercially qualified bidders shall participate in this event.

Notwithstanding anything stated above, the Purchaser reserves the right to assess bidder’s capability to perform the contract, should the circumstances warrant such assessment in the overall interest of the purchaser. In this regard the decision of the purchaser is final.

3.03 Price Bid Opening

Price Bids will be opened only for technically qualified bidders. The EMD of the bidder withdrawing or substantially altering his offer at any stage after the technical bid opening will be forfeited at the sole discretion of CPDL without any further correspondence in this regard.

CPDL reserves the right to conduct the reverse auction for the products / services being asked for in the tender instead of public opening of price bids. The terms and conditions for such reverse auction events shall be as per the Acceptance Form attached as Annexure of this document. The bidders along with the tender document shall mandatorily submit a duly signed copy of the Acceptance Form attached as Annexure as a token of acceptance for the same.

In case Reverse Auction is not concluded / conducted for any reasons, a "final no regret" financial bid in Password Protected file will be called for from all qualified bidders.

NOTE: BIDS RECEIVED AFTER DUE DATE AND TIME SHALL BE LIABLE FOR REJECTION

4.00 Award Decision:

4.01 Purchaser intends to award the Order/Contract on a lowest bid basis; however, the final decision will be based on a comprehensive evaluation of factors including cost competitiveness, compliance with technical specifications, quality, delivery, Commercial terms, bidder's capacity, and other relevant considerations as deemed by the Purchaser.

4.02 Splitting of Tendered Scope of works in two or more bidders: CPDL reserves the right to split the tender scope amongst techno- commercially qualified bidders. The purchaser reserves all the rights to award the contract to one or more bidders to meet the timelines of the projects / scope of work or nullify the award decision without any reason.

4.03 In the event of a bid being selected by the purchaser and there is subsequent DEFAULT on the bid of the prospective bidder; the prospective bidder will be required to pay purchaser an amount equal to the difference in their bid and the next lowest bid on the quantity declared in NIT/RFQ.

4.04 In case any Bidder is found unsatisfied during the delivery process, the award will be cancelled and CPDL reserves the right to award other Bidders who are found fit.

5.00 Market Integrity:

CPDL provides a fair and competitive marketplace. The rules for bidders are outlined in the Terms & Conditions. Bidders must agree to these rules prior to participating. In addition to other remedies available, CPDL reserves the right to exclude a bidder from participating in future markets due to the bidder’s violation of any of the rules or obligations contained in the Terms & Conditions. A bidder who violates the marketplace rules or engages in behaviour that disrupts the fair execution of the marketplace shall be restricted from bidding for a length of time, depending upon the seriousness of the violation. Examples of violations include, but are not limited to:

- Failure to honour prices submitted to the marketplace.

- Breach of the terms published in Request for Quotation/NIT.

6.00 Confidentiality:

All the technical, financial and legal information (as specified in Clause 30) being exchanged by the parties (Prospective Bidder and CPDL) arising out of information contained in this RFQ Tender Notification is confidential and shall not be disclosed, published or advertised in any manner without written authorization from CPDL. This includes all bidding information submitted.

All the technical, financial and legal documents (as specified in Clause 30) RFQ documents remain the property of CPDL and all the prospective bidders are required to return these documents to CPDL upon request.

Bidders who do not honour these confidentiality provisions will be excluded from participating in future bidding events.

7.00 Contact Information:

Technical or Commercial clarifications, if any, as regards to this Tender Notification shall be sought in writing and sent by post/courier/e-mail to the following address. The same shall not be communicated through phone etc.

|  | Technical | Commercial |  |
| --- | --- | --- | --- |
| Contact Person | Ashish Ranjan | Narinder Pal Singh | Chandra Sekhar Sahoo |
| Email ID | ashish.ranjan@rpsg.in | narinderpal.singh@rpsg.in | chandra.sahoo@rpsg.in |

-------------X-------------

SECTION – II: INSTRUCTION FOR BIDDERS

1.00 GENERAL:

Chandigarh Power Distribution Limited, hereinafter referred to as “The Company/CPDL” is intending to award the order for “Supply of HT and LT Cables” as per CPDL Specifications enclosed as Annexure of Bid Document.

2.00 SCOPE OF WORK

The scope of the work is as per Bill of Quantity (“BOQ”) in the tender.

3.00 DISCLAIMER

This Document includes statements, which reflect various assumptions, which may or may not be correct. Each Bidder shall conduct its own estimation and analysis and should check the accuracy, reliability and completeness of the information in this Document and obtain independent advice from appropriate sources in their own interest.

Neither Purchaser nor its employees will have any liability whatsoever to any Bidder or any other person under the law or contract, the principles of restitution or unjust enrichment or otherwise for any loss, expense or damage whatsoever which may arise from or be incurred or suffered in connection with anything contained in this Document, any matter deemed to form part of this Document, provision of Services and any other information supplied by or on behalf of Purchaser or its employees, or otherwise arising in any way from the selection process for the Supply.

Though adequate care has been taken while issuing the Bid document, the Bidder should satisfy itself that Documents are complete in all respects. Intimation of any discrepancy shall be given to this office immediately.

4.00 COST OF BIDDING

The Bidder shall bear all cost associated with the preparation and submission of its Bid and the company will in no case be responsible or liable for those costs.

5.00 BIDDING DOCUMENTS

The Scope of Work, Bidding Procedures and Contract Terms are described in the Bidding Documents. In addition to the covering letter accompanying Bidding Documents, the Bidding Documents include:

Request for Quotation (RFQ) - Section - I

Instructions for Bidders (IFB) - Section - II

Special Conditions of Contract (SCC) - Section –III

General Condition of Contract (GCC-Supply) - Section –IV

Price Bid Format – Section-V

General Formats (Appendix)- Section-VI

Technical Specifications – Section-VII

The Bidder is expected to examine the Bidding Documents, including all Instructions, Forms, Terms and Specifications. Failure to furnish all information required by the Bidding Documents or submission of a Bid not substantially responsive to the Bidding Documents in every respect will result in the rejection of the Bid.

6.00 AMENDMENT OF BIDDING DOCUMENTS

At any time prior to the deadline for submission of Bids, the Company may for any reasons, whether at its own initiative or in response to a clarification requested by a prospective Bidder, modify the Bidding Documents by amendment.

The Amendment shall form part of the Bidding Documents, pursuant to Clause 5.00, and it will be notified on the website www.chandigarhpower.com and will be binding on the prospective Bidders.

In order to afford prospective Bidders, reasonable time to make Amendment in preparing their Bids, the Company may, at its discretion, extend the deadline for the submission of Bids. The same shall be published as a corrigendum on the website www.chandigarhpower.com.

Purchaser shall reserve the rights to following:

- extend due date of submission

- modify tender document in part/whole

- cancel the entire tender

Bidders are requested to visit the Company website at www.chandigarhpower.com  regularly for any modification/clarification/ corrigendum/ addendum of the bid documents.

7.00 LANGUAGE OF BID

Refer Section – I: Request for Quotation

8.00 DOCUMENTS COMPRISING THE BID

Refer Section – I: Request for Quotation

9.00 BID FORM

Refer Section – I: Request for Quotation

9.02 EMD

The bidder shall furnish, as part of its bid, an EMD amounting as specified in the RFQ. The EMD is required to protect the Purchaser against the risk of Bidder’s conduct, which would warrant forfeiture.

The EMD shall be denominated in any of the following form:

- Bank Guarantee valid for One hundred Twenty (120) days from due date of submission or amended due date of submission. (EMD should be as per the prescribed format as mentioned in the tender document)

- Through NEFT/RTGS

The EMD may be forfeited in case of:

- The Bidder withdraws its bid during the period of specified bid validity

OR

- In the case of a successful Bidder, if the Bidder does not

- Accept the Purchase Order, OR

- Furnish the required performance security BG.

10.00 BID PRICES

10.01 Bidders shall quote for the entire Scope of Supply / Work with a break-up of prices for individual items and Taxes & Duties. The total Bid Price shall also cover all the Supplier's obligations mentioned in or reasonably to be inferred from the Bidding Documents in respect of Design, Supply, Transportation to site, in accordance with the requirement of Bidding Documents. The Bidder shall complete the appropriate Price Schedules included herein, stating the Unit Price for each item & total Price with taxes, duties & freight up to destination.

10.02 The prices offered shall be inclusive of all costs as well as Duties, Taxes and Levies paid or payable during execution of the supply work, breakup of price constituents, should be there. The Bidder is required, at his expense, to obtain all the information he may require to enable him to submit his tender including necessary visits to the site to ascertain the local conditions, procurement of necessary materials, labour, etc., requirements of the local/government/public authorities in such matters.

10.03 Prices quoted by the Bidder shall be variable as per PV clause mentioned in bid document.

11.00 BID CURRENCIES

Prices shall be quoted in Indian Rupees Only.

12.00 PERIOD OF VALIDITY OF BIDS

12.01 Bids shall remain valid for 120 days from the due date of submission of the Bid & subsequent corrigendum / amendment / extension of due date of submission.

12.02 Notwithstanding anything in Clause 12.01 above, the Purchaser may solicit the Bidder‘s consent to an extension of the Period of Bid Validity. The request and the responses thereto shall be made in writing and sent by post/courier/e-mail.

13.00 ALTERNATIVE BIDS

Bidders shall submit Bids complying with the Bidding Documents. Alternative Bids will not be considered. The attention of Bidders is drawn to the provisions regarding the rejection of Bids in the terms and conditions, which are not substantially responsive to the requirements of the Bidding Documents.

14.00 FORMAT AND SIGNING OF BID

14.01 The original Bid Form and accompanying documents, clearly marked "Original Bid" and “Copy” must be received by the Purchaser at the date, time and place specified pursuant to Clauses 15.0 and 16.0. In the event of any discrepancy between the original and the copy, the original shall govern.

14.02 The original and copies of the Bid shall be typed or written in indelible ink and shall be signed by the Bidder or a person or persons duly authorized to sign on behalf of the Bidder. Such authorization shall be indicated by written Power-of-Attorney accompanying the Bid.

14.03 The Bid should contain no interlineations, erasures or overwriting except as necessary to correct errors made by the Bidder, in which case such corrections shall be initialled by the person or persons signing the Bid.

15.00 SEALING AND MARKING OF BIDS

Refer Section – I: Request for Quotation

16.00 DEADLINE FOR SUBMISSION OF BIDS

16.01 The original Bid, together with the required copies, must be received by the Purchaser at the address specified earlier.

16.02 The Purchaser may, at its discretion, extend the deadline for the submission of Bids by amending the Bidding Documents, in which case all rights and obligations of the Purchaser and Bidders previously subject to the deadline will thereafter be subject to the deadline as extended.

17.00 ONE BID PER BIDDER

Each Bidder shall submit only one Bid by itself. No Joint Venture is acceptable. A Bidder who submits or participates in more than one Bid will cause all those Bids to be rejected.

18.00 LATE BIDS

Any Bid received by the Purchaser after the deadline for submission of Bids prescribed by the Purchaser, pursuant to Clause 16.0, will be declared "Late" and shall be rejected and returned unopened to the Bidder.

19.00 MODIFICATIONS AND WITHDRAWAL OF BIDS

19.01 The Bidder is not allowed to modify or withdraw its Bid after the Bid submission.

20.00 PROCESS TO BE CONFIDENTIAL

Information relating to the examination, clarification, evaluation and comparison of Bids and recommendations for the award of a contract shall not be disclosed to Bidders or any other persons not officially concerned with such process. Any effort by a Bidder to influence the Purchaser's processing of Bids or award decisions may result in the rejection of such Bidder's Bid.

21.00 CLARIFICATION OF BIDS

To assist in the examination, evaluation and comparison of Bids, the Purchaser may, at its discretion, ask the Bidder for a clarification of its Bid. All responses to requests for clarification shall be in writing and no change in the price or substance of the Bid shall be sought, offered or permitted.

22.00 PRELIMINARY EXAMINATION OF BIDS / RESPONSIVENESS

22.01	Purchaser will examine the Bids to determine whether they are complete, any computational errors have been made, required sureties have been furnished, the documents have been properly signed and the Bids are generally in order. Purchaser may ask for submission of original documents in order to verify the documents submitted in support of qualification criteria.

22.02 Arithmetical errors will be rectified on the following basis. If there is a discrepancy between the unit price and the total price per item that is obtained by multiplying the unit price and quantity, the unit price shall prevail and the total price per item will be corrected. If there is a discrepancy between the Total Amount and the sum of the total price per item, the sum of the total price per item shall prevail and the Total Amount will be corrected.

22.03 Prior to the detailed evaluation, Purchaser will determine the substantial responsiveness of each Bid of the Bidding Documents including production capability and acceptable quality of the Goods offered. A substantially responsive Bid is one, which conforms to all the terms and conditions of the Bidding Documents without material deviation.

22.04	Bid determined as not substantially responsive will be rejected by the purchaser and may not subsequently be made responsive by the Bidder by correction of the non - conformity.

23.00 EVALUATION AND COMPARISON OF BIDS

The evaluation of Bids shall be done based on the delivered cost competitiveness.

23.01 The evaluation of the Bids shall be a stage-wise procedure. The following stages are identified for evaluation purposes: In the first stage, the Bids would be subjected to a responsiveness check. The Technical Proposals of the Bidders would be evaluated first.

23.02 Subsequently, the Financial Proposals along with Supplementary Financial Proposals (obtained through Reverse Auction and/or Final Negotiation), if any, of Bidders with Techno-commercially Acceptable Bids shall be considered for final evaluation.

23.03 The Purchaser while evaluating the Bid will also consider, in addition to the Bid price, the following factors, in the manner and to the extent indicated in this Clause:

- Delivery Schedule

- Conformance to Qualifying Criteria

- Deviations from Bidding Documents

Bidders shall base their Bid price on the terms and conditions specified in the Bidding Documents.

The cost of all quantifiable deviations and omissions from the specification, terms and conditions specified in Bidding Documents shall be evaluated. The Purchaser will make its own assessment of the cost of any deviation for the purpose of ensuring fair comparison of Bids.

23.04 Any adjustments in price, which result from the above procedures, shall be added for the purposes of comparative evaluation only to arrive at an "Evaluated Bid Price". Bid Prices quoted by Bidders shall remain unaltered.

24.00 CONTACTING THE PURCHASER

24.01 If any Bidder wishes to contact the Purchaser on any matter related to the Bid, from the time of Bid opening to the time of contract award, the same shall be done in writing only.

24.02 Any effort by a Bidder to influence the Purchaser and/or in the Purchaser‘s decisions in respect of Bid evaluation, Bid comparison or Contract Award, will result in the rejection of the Bidder‘s Bid.

25.00 THE PURCHASER’S RIGHT TO ACCEPT ANY BID AND TO REJECT ANY OR ALL BIDS

The Purchaser reserves the right to accept or reject any Bid and to annul the Bidding process and reject all Bids at any time prior to award of Contract, without thereby incurring any liability to the affected Bidder or Bidders or without any obligation to inform the affected Bidder or Bidders of the grounds for the Purchaser‘s action.

26.00 AWARD OF CONTRACT

26.01 The Purchaser will award the Contract to the successful Bidder whose Bid has been determined to be the lowest evaluated responsive Bid, provided further that the Bidder has been determined to be qualified to satisfactorily perform the Contract. Purchaser reserves the right to award order to other bidders in the tender, provided it is required for timely execution of project & provided he agrees to come to the lowest rate.

26.02 Splitting of Tendered Scope of works in two or more bidders:

CPDL reserves the right to split the tender scope amongst techno-commercially qualified bidders. The purchaser reserves all the rights to award the contract to one or more bidders to meet the timelines of the projects /scope of work or nullify the award decision without any reason.

26.03 The Purchaser intends to issue separate Purchase / Work Orders viz.

a) Purchase Order for Supply

b) Work Order for Installation, Testing & Commissioning

27.00 THE PURCHASER’S RIGHT TO VARY QUANTITIES

The Purchaser reserves the right to vary the quantity by +/- 25% i.e. increase or decrease the numbers/ quantities without any change in terms and conditions during the execution of this document and amendments thereof.

28.00 LETTER OF INTENT/ NOTIFICATION OF AWARD

The Letter of Intent / Notification of Award shall be issued to the successful Bidder whose bids have been considered responsive, techno-commercially acceptable and evaluated to be the lowest (L1). The successful Bidder shall be required to furnish a letter of acceptance within 7 days of issue of the letter of intent / Notification of Award by Purchaser. The date of LOI / LOA shall be treated as Start date of work.

29.00 PERFORMANCE BANK GAURANTEE

Within fifteen (15) days from the date of receipt of the Purchase Order / Work Order, the successful Bidder (either Authorized channel partner or OEM) shall furnish a Performance Bank Guarantee (PBG) towards the faithful performance of the contract, for an amount equal to 5% (Five percent) of the supply order value (inclusive of taxes). The PBG shall be submitted on a pro-rata basis, corresponding to the released order value, and shall remain valid until the expiry of the warranty period, plus an additional three (3) months as a claim period.

30.00 CORRUPT OR FRADULENT PRACTICES

30.01	The Company requires that the Bidders observe the highest standard of ethics during the procurement and execution of the Project. In pursuance of this policy, the Company:

- Defines, for the purposes of this provision, the terms set forth below as follows:

- "Corrupt practice" means behaviour on the part of officials in the public or private sectors by which they improperly and unlawfully enrich themselves and/or those close to them, or induce others to do so, by misusing the position in which they are placed, and it includes the offering, giving, receiving, or soliciting of anything of value to influence the action of any such official in the procurement process or in contract execution; and

- "Fraudulent practice" means a misrepresentation of facts in order to influence an award process or the execution of a contract to the detriment of the Company, and includes collusive practice among Bidders (prior to or after Bid submission) designed to establish Bid prices at artificial non-competitive levels and to deprive the Company of the benefits of free and open competition.

- Will reject a proposal for award if it determines that the Bidder recommended for award has engaged in corrupt or fraudulent practices in competing for the contract in question;

- Will declare a firm ineligible, either indefinitely or for a stated period of time, to be awarded a contract if it at any time determines that the firm has engaged in corrupt or fraudulent practices in competing for, or in executing, a contract.

30.02 Furthermore, Bidders shall be aware of the provision stated in the Terms and Conditions of Contract.

31.00 DELIVERY PERIOD

For LT Cable:

Bidders shall supply material within 6 to 8 Weeks from the date of issuance of LOI / Release Order/manufacturing Clearance against Rate Contract. However, firm delivery dates will be mentioned in the LOI / Order.

For HT Cable:

Bidders shall supply material within 8 to 10 Weeks from the date of issuance of LOI / Release Order/manufacturing Clearance against Rate Contract. However, firm delivery dates will be mentioned in the LOI / Order.

##### PRIORITY OF CONTRACT DOCUMENTS

The several documents forming the Agreement are to be taken as mutually explanatory of one another, but in case of ambiguities or discrepancies, the same shall be explained and adjusted by the Company, who shall, accordingly, issue suitable instructions thereon to the Bidder/Supplier. In such event, unless otherwise provided in the agreement or explained by way of instructions by the Company, as mentioned above, the priority of the documents forming the Agreement shall be as follows:

    - Contract Agreement / Purchase Order. (a) Special Conditions of Contract (b) General Conditions of Contract;

    - The Tender document, including all Appendices and/or Addenda, Corrigendum the latest taking precedence;

    - The Letter of Acceptance / Intent;

    - Agreed Minutes of the Tender Negotiation Meeting;

    - Agreed Minutes of the Tender Technical Meetings;

    - The Priced Bill of Quantities;

    - The Technical Specifications / Scope of work;

In the event of any conflict between the above-mentioned documents, the more stringent requirement or conditions which shall be favorable to the Company shall govern and the decision of CPDL shall be final and binding upon the parties.

--------------X--------------

Section – III: SPECIAL TERMS AND CONDITIONS OF CONTRACT

Special conditions of contract, if any shall be communicated along with issuance of LOI /PO.

Section – IV: GENERAL TERMS AND CONDITIONS OF CONTRACT (GCC)

Table of Contents

- Definition of Terms

- Price Basis

- Taxes & Duties and Statutory Variation

- Variation in Taxes, Duties and Levies

- Taxes & Duties on Raw Materials & Bought Out Components

- Packing & Forwarding Charges

- Freight Charges

- Transit Insurance

- Unloading Charges

- Documentation

- Purchase Order Amendments

- Product Specifications

- Subcontracting

- Quality Assurance and Inspection

- Rejection

- Delivery

- Dispatch Documents

- Contract Performance Bank Guarantee

- Payment Terms

- Transfer of Title

- Warranty/Defect Liability Period

- Liquidated Damages

- Demurrage on non/Delayed Collection of Rejected and Excess Material

- Limitation of Liability

- Force Majeure

- Supplier’s Default & Risk Purchase

- Suspension

- Termination

- Arbitration

- Confidentiality

- Recoveries

- Compliance with Applicable Laws

- Governing Law and Jurisdiction of Contract

- Indemnification

##### Termination for Convenience of Purchaser

##### Purchase Order Acceptance

##### Following Annexures Enclosed With GCC

##### Annexure 1: Sustainable Procurement Policy

##### Annexure 2: Acceptance Form for Participation in Reverse Auction Event

##### Annexure 3: Manufacturer Authorization Form

##### Annexure 4: Deviation Sheet

##### Annexure 5: Format for Contract Performance Bank Guarantee

##### Annexure 6: Format of Warranty/Guarantee Certificate

##### Annexure 7: Mutual Non-Disclosure Agreement

##### DEFINITION OF TERMS

Chandigarh Power Distribution Limited also referred to as CPDL is a Power Distribution Licensee of the Chandigarh Region and is having its registered office at SCO 33-35, 4th Floor, Sector 34-A Chandigarh - 160022, India.

Purchaser shall mean Chandigarh Power Distribution Limited, on whose behalf this bid enquiry is issued by its authorized representative / officers.

Bidder shall mean the firm who quotes against this bid enquiry issued by the Purchaser.

Supplier shall mean the successful Bidder, an individual or firm or company whether incorporated or not on whom the Purchase Order is placed by CPDL and shall include their legal successors and assigns, its affiliates and their respective employees, officers, directors, agents and representatives.

Party / Parties shall mean CPDL and / or the Supplier, as the context requires.

Purchase Order shall mean the order placed by CPDL and accepted by Supplier or agreement entered into between CPDL and Supplier including all attachments, schedules and annexure thereto and all documents incorporated by reference therein together with any subsequent modifications thereof in writing.

Sub-vendor/Sub-contractor shall mean the individual or firm or company (other than the Supplier or CPDL) to whom the Supplier has sub-let any part of the Supplies or with whom the Supplier has entered into any sub-contract for the Supply of equipment, material or services in connection with the Supplies, and shall include their legal successors and assigns.

Supply/Supplies shall mean all the Supplies, to be executed by the Supplier as per the Purchase Order.

Good Industry Practice means those reasonable and prudent applicable engineering codes and standards, practices, methods, equipment, specifications and standard of performance and safety generally used by professional organization performing design, procurement, engineering, manufacturing, construction as the case maybe, in the international design, procurement, engineering and manufacturing and construction industries in relation to equipment/packages of the same or substantially similar scale, nature and complexity.

##### PRICE BASIS

After finalization of the tender, Rate Contract shall be issued to the successful bidder with a validity period of Two Years. Release order shall be placed as per the requirement of CPDL.  The price shall be variable and price variation clause shall be as per latest IEEMA price variation formula. However, the current applicable PV clause is mentioned below;

For LT Cable: Reference No: 35/DIV/CAB/05, Dated 24.04.2018: (Attached Separately)

For HT Cable: Reference No: 91/DIV/CAB/05, Dated 09.10.2019: (Attached Separately)

All #0# denoted input prices in the formula (Al0, Cu0, Fe0, CC0, PVC0 etc.) shall be as per IEEMA Circulars of June-25 (Published in July 2025).

All input prices in the formula (Al, Cu, Fe, CC, PVC etc.) shall be as per IEEMA Circular for the month of manufacturing clearance/delivery confirmation (published in subsequent month) There will be no cap on Positive side and negative side.

The Bidder shall indicate the applicable taxes and duties on the finished supplies separately in the Price Schedule. However, the quoted price shall be inclusive of all the taxes, duties and cess of any kind levied by any central, municipal or other government authority on raw materials & components including imports, if any.

The Bidder shall be deemed to have understood all technical, commercial, general and special purchase conditions for the Supply. The Bidder shall not, except as expressly provided in the Purchase Order, be entitled to any extension of the delivery Schedule or to any adjustment of the Contract Price on grounds of misinterpretation or misunderstanding of any such matter.

Prices and discounts, if any, must remain the same for any additional quantities of similar items required, if repeat order is placed within Six (6) months of the original Purchase Order.

Unit prices and discounts, if any, shall be applicable for ordering without any stipulation of minimum order value or on the basis of total order for items tendered.

##### TAXES & DUTIES AND STATUTORY VARIATIONS

The prices are subject to all direct tax and indirect tax provisions as applicable on the date of transaction.

However, the same would be paid at actuals provided the material is delivered as per the original/ extended delivery schedule provided in the Purchase Order. CPDL shall not be liable to pay any increase in taxes & duties beyond the delivery schedule provided in the Order, however, benefit due to any downward revision in statutory rates shall be passed on to CPDL

##### VARIATION IN TAXES, DUTIES AND LEVIES

The total order value shall be adjusted on account of any variations in Statutory Levies imposed by Competent Authorities by way of fresh notification(s) within the stipulated delivery period only. In case of reduction in taxes, duties and levies, the benefits of the same shall be passed on to CPDL.

No other Taxes, Duties & Levies other than those specified in the Purchase Order will be payable by CPDL except in case of new Levies, Taxes & Duties imposed by the Competent Authorities by way of fresh notification(s) subsequent to the issue of PURCHASE ORDER but within the stipulated delivery period.

Notwithstanding what has been stated above, changes in Taxes, Duties & Levies shall apply only to that portion of PURCHASE ORDER not executed on the date of notification by Competent Authority. Further, changes in Taxes, Duties & Levies after due date of Delivery shall not affect PURCHASE ORDER Terms and Value.

PURCHASE ORDER value shall not be subject to any variation on account of variation in Exchange rate(s).

##### TAXES & DUTIES ON RAW MATERIALS & BOUGHT OUT COMPONENTS

Taxes & Duties on raw materials & bought out components are included in Purchase Order Value and are not subject to any escalation or variation for any reason whatsoever.

Taxes & Duties on raw materials & bought out components procured indigenously are included in Purchase Order Value and are not subject to any escalation or variation for any reason whatsoever.

##### PACKING & FORWARDING CHARGES

Charges towards packing, forwarding and loading is included in the Total Order value.

Packing: Supplier shall pack or shall cause to be packed all Commodities in crates/boxes/drums/containers/cartons and otherwise in such a manner as shall be reasonably suitable for shipment by road or rail to CPDL, Chandigarh stores/site without undue risk of damage in transit. All the packaging materials as prescribed shall be supplied preferably with bio-degradable packing- materials.

Packing List: The contents of each package shall be itemized on a detailed list showing the exact weight, extreme outside dimensions (length, width & weight) of each container/box/drum/carton, Item SAP Code, PO No & date. One copy of the packing list shall be enclosed in each package delivered.

##### FREIGHT CHARGES

The total order is inclusive of freight charges. The responsibility of transportation of material from its source to CPDL's stores / specified site, safely and securely is entirely the responsibility of the supplier. During transportation, the supplier is responsible for complying with the provisions of Motor Vehicle Act and various other statutory norms related to weight, measurement, vehicle age and pollution monitoring, safe transportation etc.

##### TRANSIT INSURANCE

Cost of Transit insurance is included in the Total order value.  The Supplier shall fully insure the Goods, at their own expense, from the time of dispatch until the Goods are delivered, offloaded, and successfully commissioned at the destination. The insurance should cover any damage or loss that may occur during this period.

##### UNLOADING CHARGES

Supplier shall be responsible for safe unloading of the material at CPDL Store/ specified Site, at their own cost.

##### DOCUMENTATION

Purchase Order number must appear in all correspondences, drawings, invoices, despatch notes, packing lists and on any other document(s) related to the Purchase Order.

The technical specifications, drawings and documents, Quality Assurance & Inspection Plan (QAP), installation, operation and maintenance manuals including spare part lists (if any) shall be furnished by the Supplier in required number of copies and within time period as specified in delivery schedule/Purchase Order.

Material Safety Data Sheet (MSDS), detail handling & storage instruction sheet/manual, wherever applicable, to be furnished before commencement of supply and one copy is to be submitted in store/site with First Lot.

##### PURCHASE ORDER AMENDMENTS

The Purchase Order may, in writing, be amended or modified including changes in contract price, technical specifications, quantities and terms and conditions based on mutual agreement by an amendment to the original Purchase Order, issued by CPDL and accepted by the Supplier.

The Supplier shall not be required to implement any variation until an instruction to execute such variation has been issued by CPDL.

The Supplier may also make a request for a change if required, through a change proposal note indicating nature of the change(s), reasons for the change(s), its impact on the price, the delivery schedule and/or the guarantees together with supporting documents. CPDL shall assess Supplier’s request for a change and communicate acceptance/otherwise. Supplier shall not implement any change without obtaining CPDL’s prior approval in writing.

The Supplier shall bring to the notice of CPDL along with documentary evidence, should any changes in the codes and standards applicable to the Purchase Order occur after the date of Purchase Order. The Supplier shall comply with the changes only after receipt of CPDL’s approval.

##### PRODUCT SPECIFICATIONS

The Supplier shall be solely responsible for supply of material fully compliant with approved technical specifications, applicable codes and standards and approved drawings stated in the Purchase Order with the approved makes of various components and make the same functional.

Supplier shall provide manuals (one set Soft copy and 2 sets Hard copy) containing complete specifications, instructions and other key points with respect to the material supplied, its usage, installation, operation and maintenance manual within 7 days from the date of the Delivery of the material.

Unauthorized substitution/supplies with wrong description and quality, excess Supplies, rejected Supplies shall be returned to the Supplier at the risk and expenses of the Supplier including transportation from and to their workshop.

Supplier(s) shall not be relieved of their obligations under the Purchase Order, including but not limited to its guarantee and obligations stated herein, by incorporating CPDL’s technical comments on their drawings and documents during execution of the Purchase Order.

Supplier shall be deemed to have scrutinized all data and information provided by CPDL regarding accuracy and adequacy. CPDL shall not be responsible for any error, inaccuracy or omission of any kind and shall not be deemed to have given any representation of accuracy or completeness of any data or information. Any data or information received by the Supplier from CPDL shall not relieve the Supplier from its responsibility.

##### SUBCONTRACTING

The Supplier shall not sub-contract all of the Supply to third parties for the completion of the Purchase Order.

The Supplier shall submit along with their quotation, the list of proposed sub-contractor(s)/Sub-vendor(s) for the bought-out items to be procured by the Supplier, which shall be mutually discussed and agreed before placement of Purchase Order. CPDL and Supplier may by mutual agreement add or delete Sub vendors from the approved list during execution of the Purchase Order.

The Supplier indemnifies and shall keep indemnified CPDL against any losses, damages, claims or such other implications arising from or out of the acts and omissions of such sub-contractor/sub-vendor. The Supplier shall be responsible for making all payments to the sub-contractor/sub-vendor as may be necessary, in respect of any Services performed or task executed, and CPDL shall not be responsible for any part or full payment which is due to such sub-contractor.

The approval of the sub-contractors/sub-vendors list by CPDL shall not discharge the Supplier from any or all of its contractual obligations.

Any subcontract and/or suborder shall necessarily include the same obligations as those to which the Supplier has agreed in the Purchase Order, provided they are applicable to said subcontract and/or suborder. The Supplier shall ensure that said subcontract and/or suborder are compatible with the Purchase Order.

Neither Party shall be deemed by virtue of the Purchase Order to have any contractual obligations to or relationship with any sub-contractor/sub-vendor of other Party.

The Supplier shall take all measures to ensure necessary coordination with Sub-contractor/sub-vendor, and shall in any event remain fully responsible and accountable for the Purchase Order.

The Supplier shall not be entitled to change the place(s) of carrying out of the manufacturing of Supply as specified in the Purchase Order, except with CPDL prior written agreement.

Upon CPDL's request, the Supplier shall provide un-priced copy of the sub-contract and/or sub-order to CPDL.

##### QUALITY ASSURANCE AND INSPECTION

The Supplier shall ensure that the quality of material /services are strictly as per the technical and other standards specified by CPDL in Tender/RFQ/Purchase Order. In case of any deficiency/ non-conformity, the CPDL, at its sole discretion, may either reject such materials/ services in part/ full or accept the same with penalty/ compensation in lieu of the above along-with applicable taxes.

All the Supplies shall be inspected and tested by CPDL as per approved QAP (Quality Assurance Plan) during execution of the Purchase Order and prior to dispatch. All relevant inspection documents like Material Test Certificates, internal inspection and test reports are to be made available to CPDL’s inspectors at the time of inspection.

All tests as per approved QAP, applicable codes and as required by statutory authorities shall be performed by the Supplier at their cost.

CPDL Inspectors are authorised to reject the use and despatch of any Supplies which have failed during inspection and tests and do not comply with the specifications, codes and testing requirements.

The Supplier shall inform CPDL by E-mail, at least ten days in advance of the contact person details, telephone nos., exact place, date and time of rendering the Supplies for inspection.

Supplier shall bear all expenses for the additional visits (if any) for the repeat inspection and testing of the Supplies either due to non-readiness or failure during the inspection and testing.

The Supplier shall provide free access to CPDL inspectors during normal working hours to Supplier’s or their Sub-vendor’s works. The Supplier shall ensure that all useful means of performing, checking, marking, testing, inspection and final testing are provided to the inspectors.

CPDL has no obligation to discover defects or otherwise and it shall be sole responsibility of Supplier even if the inspections and tests are fully carried out. CPDL’s inspection shall not absolve the Supplier of its obligations to ensure that all Supplies strictly comply with the requirements as per the Purchase Order.

Delay in delivery, if any, due to delay in offering the Supplies for test and inspection for the reasons attributable to Supplier, shall be at the risk, expenses and responsibility of the Supplier.

CPDL may decide not to inspect the material, in which case it will convey its decision of waiver of inspection in writing.

The performance of waiver of QA activity by CPDL at any stage of manufacturing does not relieve the supplier of any obligation to perform in accordance with and meet all the requirements of the procurement documents and also all the codes & reference documents mentioned in the procurement document nor shall it preclude subsequent rejection by the CPDL.

On completion of manufacturing the items can only be dispatched after receipt of dispatch Instructions issued by the Purchaser.

All in-house testing and inspection shall be done without any extra cost. The in-house inspection shall be carried out in presence of CPDL inspector.

##### REJECTION

CPDL reserves the right to reject all or part of the Supplies which is not in conformity with the Purchase Order and the Supplier is not able to rectify the non-conformity in reasonable time after a formal notice in writing is issued to the Supplier by CPDL.

The rejection of the Supplies or part thereof shall be notified to the Supplier in writing. Supplier shall be provided option of replacing the same as soon as possible within agreed time limit at their own risks and expenses.

In case Supplier fails to replace the Supply within mutually agreed time limit, CPDL shall get the Supply replaced at Supplier’s risk and cost including exercising of CPDL’s rights under clause “Liquidity Damages”.

Notwithstanding the above, CPDL may temporarily use all or part of the rejected Supply until the same is replaced by the Supplier.

Notwithstanding any objection from the Supplier, title to the rejected Supply shall automatically be transferred back to the Supplier by simple written notice from CPDL.

The Supplier shall then, at their expense and at their own risk & cost, take back the rejected Supply wherever made available by CPDL.

##### DELIVERY

The delivery schedule will be strictly as per our requirements specified in the Purchase Order. If the Supplier anticipates any delay in the delivery, they must inform CPDL in writing immediately. Such notification shall not constitute an extension of the delivery schedule

The material shall be delivered at CPDL's stores / specified site during the business hours along with invoice, challan, Insurance documents, road permit and a copy of this Order to facilitate the process of unloading and receiving of material as per the terms of this Order.

Supplier, if reasonable and practicable, may affect partial despatches of the Supplies with prior approval from CPDL. Delivery challan, excise invoice and packing list must accompany each consignment.

The Supplier shall not make the Supply available for transport or dispatch the Supply directly without CPDL's prior written consent, failing which CPDL reserves the right to return the Supply to the Supplier at Supplier’s risk and expense.

If the delivery is not made at the said location and/or within the allotted period of time, any costs incurred by CPDL in connection with dead freight, demurrage, warehousing, insurance, carriage to another loading point and/or any other associated costs to ensure the delivery, shall be borne by the Supplier.

The Supplier shall inform, telephonically as well as through e-mail, to the Store in-charge regarding the delivery/ dispatch of materials at least 3 days in advance to make necessary arrangement for unloading of material.

If the Supplier fails to deliver the material in time, CPDL may, at its sole discretion:

- treat the order as cancelled at any time and recover any loss or damage from the Supplier;

- purchase the material ordered or any part thereof from other sources on the Supplier's account, in such case, the Supplier shall be liable to pay CPDL not only the difference between the price at which such material have been actually purchased and the price calculated at the rate set out in this order, but also any other loss or damage that CPDL may suffer.

##### DESPATCH DOCUMENTS

Dispatch instructions given in the Purchase Order shall be strictly followed. Failure to comply with instructions of the dispatch instructions shall result in delay in payment against invoices.

##### PERFORMANCE BANK GUARANTEE

Within fifteen (15) days from the date of receipt of the Purchase Order / Work Order, the successful Bidder (either Authorized channel partner or OEM) shall furnish a Performance Bank Guarantee (PBG) towards the faithful performance of the contract, for an amount equal to 5% (Five percent) of the supply order value (inclusive of taxes). The PBG shall be submitted on a pro-rata basis, corresponding to the released order value, and shall remain valid until the expiry of the warranty period, plus an additional three (3) months as a claim period.

##### PAYMENT TERMS

For Supply:

For the purpose of processing the payment, the Supplier shall, upon delivery of the material in proper condition, submit the following documents in original at CPDL’s office Address, i.e., "Chandigarh Power Distribution Limited, SCO 33-35, 4th Floor, Sector 34-A, Chandigarh - 160022, India.

- Original Invoice in the name of M/s Chandigarh Power Distribution Limited, Bills/ invoices shall mention Supplier's GSTIN'.;

- Delivery Challan/E way Bill.

- Guarantee/Warrantee Card.

- Test Reports

- Copy of Order.

- Dispatch Instructions

Upon submission of the aforesaid documents, payment will be released as per the following milestone basis:

- 20% of contract value will be paid as interest free advance against Corporate Guarantee / Advance Bank Guarantee of an Equivalent amount from nationalized / scheduled bank(s) as may be acceptable to the Company, initially valid for a period of nine months from the date of submission.

- 70% Payment shall be released on pro-rata basic within 90 days from the receipt of material at CPDL site with complete set of documents as mentioned in order. Supplier should submit the invoices along with all required documents at CPDL Office within 3 days. Any delay in submission of any of these documents will be to your account. It may please be noted that for payment purposes the date of receipt of documents will be considered on the basis of the date of receipt of last document, in case partial documents were received earlier.

- The remaining 10% shall be released after submission of Performance Bank Guarantee (PBG).

##### TRANSFER OF TITLE

The Supplies shall be consigned to CPDL and the title of the Supplies shall be passed to CPDL. However, such passing of the Title of Ownership to the CPDL shall not in any way absolve, diminish or dilute the responsibility and obligation of the Supplier, as per Purchase Order.

The Supplies shall be guaranteed to be free of any lien, encumbrance or pledge.

In the event of a subcontract or suborder, the Supplier shall be required to include in its favour the same provision in respect of transfer of title.

##### WARRANTY/DEFECT LIABILITY PERIOD

The Supplier shall guarantee that the material supplied under this Purchase Order is free from any defect relating to design, manufacturing, material, construction, erection, installation, workmanship & quality and is capable of its due, rated and intended quality performance, as an integrated product for a period of 60 months from the date of commissioning or 66 months from the date of delivery; whichever is earlier, termed as Warranty Period.

LATENT DEFECT: Hidden defects in manufacturing or design of the material supplied and which could not be identified by the tests conducted but later manifested during operation of the material are termed as latent defects. The supplier shall further be responsible for free replacement for another period of Five years from the end of the guarantee period for any Latent Defects if noticed and reported by CPDL.

If any trouble or defect, originating with the design, material, workmanship or operating characteristic arises at any time during the warranty period, the Supplier shall be notified thereof. Supplier shall at their own expense and as promptly as possible make such alterations, repairs and replacements as may be necessary to permit the Supply to function in accordance with the specifications and to fulfil the guarantees. Any item so replaced, repaired and altered shall be delivered on CPDL Store/Site, with no cost implication to CPDL’s account.

CPDL shall notify the Supplier of any defect/discrepancies noticed during construction, start up and operation and the warrantee period. If the Supplier fails to commence and proceed diligently with the remedy of any such defect within 15 days of receipt of notification thereof from CPDL, CPDL may proceed to do the repair at the Supplier’s expense provided that it is done in a reasonable manner in accordance with Good Industry Practice, while notifying the Supplier of its intention to do so and permitting the Supplier to inspect such repaired or replaced Supply to ensure that the quality standards have been maintained. The reasonable cost so incurred by CPDL shall be deducted from the payables or to be paid by the Supplier to CPDL or from any of the bank guarantee provided by the Supplier.

Wherever it is established that a defect in Supply is due to faulty design, the Supplier shall replace all identical Supplies performing the same function under the same working conditions with new ones based on the correct design, even though, such Supplies may not have given rise to any failure.

##### LIQUIDATED DAMAGES

Timely delivery of material is the essence of the Purchase Order. The Supplier shall be responsible for timely delivery of material as per the specified delivery schedule. In case of delay in supply, the supplier shall be liable to pay liquidated damages @ 0.5% of all-inclusive value of the delayed material for each week of delay or part thereof subject to a maximum of 5% plus applicable GST, beyond which CPDL will be free to terminate the Purchase Order without any liability or compensation.

##### DEMURRAGE ON NON/DELAYED COLLECTION OF REJECTED AND EXCESS MATERIAL

The Supplier shall be responsible for lifting the rejected/ excess material within 10 working days from the date of intimation by CPDL. In case, such material is not lifted by Supplier within the prescribed time, it shall be liable to pay demurrage/ warehouse charges @ 1% per week of all-inclusive value of such material subject to maximum of 8% plus applicable GST thereon. In case the said material is not lifted within 8 weeks from the date of intimation, CPDL will be free to dispose-off the said material as scrap and/or destroy the same as it may deem fit. However, demurrage charges will be recovered from the Supplier. No claim for collection of rejected/excess material shall be entertained after expiry of 8 weeks.

##### LIMITATION OF LIABILITY

The Supplier shall be liable to CPDL for any damage occurring during the implementation of the Purchase Order until defect free delivery, and, in as much as the Supplier is at the origin thereof, for damage resulting from the use of the Supplies after delivery and during the warranty period.

It is understood that the Supplier's liability for damage referred to in the present clause, shall extend to any action, omission, error or negligence of its agents, Sub-vendors/Sub-contractors, and, more extensively, to any person for whom it is responsible.

The Supplier shall be liable to third parties for the consequences of any damage incurred by such third parties if caused by the Supplier as a result of or during the performance of its activities or obligations under the Purchase Order.

The Supplier shall defend, indemnify and hold CPDL harmless, without any limit, from and against any and all claims, suits and the like, including reasonable attorney fees, brought against CPDL arising out of or in connection with Supplier’s liability as stated above.

The Supplier's maximum aggregate liability shall not exceed the total contract price. The limitation of liability shall not apply in the case of:

- liability for indemnities

- liability for fraud

- liability for wilful misconduct

- liability for gross negligence

- liability in respect of abandonment of the Purchase Order

- liability in respect to any infringement of patent rights

- any fines or penalties imposed by a relevant authority

Notwithstanding any provision to the contrary elsewhere in this Purchase Order and whether or not resulting from or contributed to by any negligence and/or breach of duty (statutory or otherwise), in no event shall either CPDL or the Supplier be liable to each other whether in Purchase Order, tort or otherwise at law, for any consequential or indirect loss arising out of or in connection with the performance of this Purchase Order. The Supplier shall also not have any claim on any account whatsoever under the Purchase Order.

##### FORCE MAJEURE

An “Event of Force Majeure” shall mean any event or circumstance not within the reasonable control, of the Party affected, but only if and to the extent that:

(i) Such event or circumstance, despite the exercise of reasonable diligence, could not have been prevented, avoided or reasonably foreseen by such Party;

(ii) Such event or circumstance materially and adversely affects the ability of the affected Party to perform its obligations under this Contract, and the affected Party has taken all reasonable precautions, due care and reasonable alternative measures in order to prevent or avoid the effect of such event on the affected parties’ ability to perform its obligations under this Contract and to mitigate the consequences thereof. For the avoidance of doubt, if such event or circumstance would not have materially and adversely affected the performance of the affected party had such affected party followed good industry practice, such event or circumstance shall not constitute force majeure.

(iii) Such event is not the direct or indirect result of the failure of such Party to perform any of its obligations under this Contract; and

(iv) Such Party has given the other Party prompt notice describing such events, the effect thereof and the actions being taken in order to comply with above clause

Specific Events of Force Majeure:

Subject to the provisions of above clause, Events of Force Majeure shall include only the following to the extent that they or their consequences satisfy the above requirements:

The following events and circumstances:

e) Effect of any natural element or other acts of God, including but not limited to storm, flood, earthquake, lightning, cyclone, landslides or other natural disasters, and

f) Explosions or fires

g) Declaration of the Site as war zone.

h) Any order, regulation, directive, requirement from any Governmental, legislative, executive or judicial authority.

Notice of Events of Force Majeure

If a force majeure event prevents a party from performing any obligations under the Contract in part or in full, that party shall:

(i) Immediately notify the other party in writing of the force majeure events within 2 working days of the occurrence of the force majeure event

(ii) Be entitled to suspend performance of the obligation under the Contract which is affected by force majeure event for the duration of the force majeure event

(iii) Use all reasonable efforts to resume full performance of the obligation as soon as practicable

(iv) Keep the other party informed of all such efforts to resume full performance of the obligation on a regular basis

(v) Provide prompt notice of the resumption of full performance or obligation to the other party.

Mitigation of events of force majeure:

The Contractor shall:

(i) Make all reasonable efforts to prevent and reduce to a minimum and mitigate the effect of any delay occasioned by an Event of Force Majeure, including applying other ways in which to perform the Contract;

(ii) Use its best efforts to ensure resumption of normal performance after the termination of any Event of Force Majeure and shall perform its obligations to the maximum extent practicable as agreed between the Parties; and Keep the Company informed at regular intervals of the circumstances concerning the event of Force Majeure, with best estimates as to its likely continuation and what measures or contingency planning it is taking to mitigate and or terminate the Event of Force Majeure.

Burden of proof:

In the event that the Parties are unable in good faith to agree that a Force Majeure event has occurred to an affected party, the parties shall resolve their dispute in accordance with the provisions of this Contract. The burden of proof as to whether or not a force majeure event has occurred shall be upon the party claiming that the force majeure event has occurred and that it is the affected party.

Terminations for certain events of force majeure:

If any obligation of any Party under the Contract is or is reasonably expected to be delayed or prevented by a Force Majeure event for a continuous period of more than 1 (one) month during the Term of the Contract, the Contract shall be terminated at the discretion of the Company and neither Party shall be liable to the other for any consequences arising on account of such termination.

##### SUPPLIER’S DEFAULT & RISK PURCHASE

Supplier shall deemed to be at default in the following cases:

- have voluntarily commenced winding-up, bankruptcy, insolvency, reorganization, stay, moratorium or similar debtor-relief proceedings, or shall have become insolvent or is unable to pay its debts as they become due, or admit in writing its inability to pay its debts or makes an assignment for the benefit of its creditors.

- obvious failure likely to affect the quality and conformity of the Supply,

- delay in the implementation of the Purchase Order, leading to an unavoidable and unreasonable postponement of the delivery schedule and/or performance tests and/or Supplier's obligations herein,

- non-implementation of the Purchase Order in whole or in part,

- Serious and/or prolonged failure of the Supplier to meet its obligations herein.

- Sub-lets and /or assigns any further part of the Purchase Order without the prior written approval of CPDL

- Non-compliance of the Mutual Non-Disclosure Agreement.

CPDL shall notify any default to the Supplier in writing. The Supplier shall promptly inform CPDL in writing of the effects of its default and of the measures it intends to take in order to correct such default as soon as possible.

If, following the receipt of a formal notice from CPDL, the Supplier fails to correct the default; CPDL may, as the case may be, upon expiry of the period of time stated in the notice and without prejudice to the possible termination of the Purchase Order in accordance with clause of GCC.

- either impose technical assistance to the Supplier without releasing the Supplier from its obligations or liability; or,

- substitute itself to the Supplier in the performance of all or part of the Supply, at the Supplier's expenses and risks, and without the Purchase Order ceasing to be valid. In this respect, CPDL may use its own resources to complete the said Supply and/or use any other third Party for this purpose by means of a subcontract,

All the costs borne by CPDL as a result of the Supplier's default shall be charged to the Supplier. Without prejudice to any other method of recovery available to CPDL, they shall be deducted from the amounts that may still be due to the Supplier by CPDL and corresponding to that part of the Supply already performed in accordance with the Purchase Order.

##### SUSPENSION

CPDL shall have the sole discretion to suspend all or part of the Purchase Order at any time. The Supplier shall temporarily stop the execution of the affected Supply. Said suspension shall take effect on the date of receipt of the written notice sent by CPDL to the Supplier. During the suspension, the obligations arising from the Purchase Order shall be suspended as regards the concerned part of the Supply, except those relating to confidentiality, insurance, patents and the protection of the supply.

The implementation of the Purchase Order shall be resumed upon issuance of a written notice to the Supplier within 60 days from the date of written notice for suspension issued by CPDL. In case, the Supplier refuses to resume the implementation of the Purchase Order without a legitimate reason, clause “SUPPLIER’S DEFAULT & RISK PURCHASE” shall automatically apply.

In case of suspension of the Purchase Order is for more than 60 days, in the absence of Supplier's default, CPDL shall provide an extension to the delivery period as mutually agreed by CPDL and Supplier on case to case basis.

Should the suspension of the Purchase Order, in the absence of Supplier's default, last more than 120 days, CPDL and Supplier shall agree upon the basis of continuation of the Purchase Order or both the parties are not able to come to an agreement, the Purchase Order shall automatically be terminated as per clause of GCC.

In the event of Suspension of Purchase Order due to Supplier’s Default, Supplier shall be fully responsible for its default pursuant to clause “SUPPLIER’S DEFAULT & RISK PURCHASE”.

##### TERMINATION

In the event of a default as described in clause “SUPPLIER’S DEFAULT & RISK PURCHASE” here above, CPDL shall have the right to terminate all or part of the Purchase Order.

The termination of the Purchase Order shall be notified to the Supplier through an email or register post. This termination shall not give rise to any indemnity in Supplier's favour.

The Supplier shall indemnify CPDL for all damages incurred by Supplier as a result of such termination including but not limited to the extra expenses resulting from the choice of another Supplier and the associated delays.

This termination shall be without prejudice to the application of penalties for late delivery and the reimbursement of the advance and/or down payments received by the Supplier for the non-completed portion of the Purchase Order.

In the absence of a Supplier's default, CPDL reserves the right to terminate all or part of the Purchase Order at any time.

In this case, CPDL shall pay the Supplier, after submission of substantiating documents accepted by CPDL, the amounts due in consideration of the work already performed and accepted by CPDL on the date of termination, after deduction of advance and/or down payments already made.

Within fifteen (15) days after the date of receipt by the Supplier of the notice of termination sent by CPDL the Supplier shall

- Cease performance of the Purchase Order or such part thereof as may be specified in the notice with immediate effect.

- Allow CPDL or its nominee full right of access to the Supplier's premises to remove all or any of CPDL's property and in order to do so use such of the Supplier’s equipment as may be necessary. CPDL shall have the right to complete balance works with the help of third parties at its own discretion.

- Assign to CPDL or its nominee to the extent desired by CPDL all or the relevant part of the rights, titles, liabilities and subcontracts relating to the Purchase Order which the Supplier may have acquired or entered into.

- Promptly deliver to CPDL, in hard copy

- and native format, all design data, design standards, drawings, specifications, requisitions, calculations, other documents and computer software prepared under the Purchase Order up to the date of termination.

- Supplier shall return all documents, drawings, information that is provided to the Supplier (without Supplier retaining any copies of the same) to CPDL.

##### ARBITRATION

All disputes if any arising out of or in connection with this order, including any question regarding its existence, validity or termination, shall, unless amicably settled between the parties, be finally settled by arbitration. The parties shall mutually agree and appoint a sole arbitrator. Notwithstanding to what is stated above, if the parties cannot mutually agree on arbitrator within 4(four) weeks from the date of invocation of arbitration, then the Arbitrator shall be appointed in accordance with rule of Arbitration and Conciliation Act 1996 {amended from time to time}. The arbitration proceedings shall be conducted as per the Arbitration and Conciliation Act 1996 {as amended}, and any modifications thereto and re-enactments thereof. The seat of arbitration shall be Chandigarh. The language to be used in arbitration proceedings shall be English. The decision of the Arbitrator shall be binding on the parties.

##### CONFIDENTIALITY

The technical information, drawing and other related documents forming part of Purchase Order and the information obtained during the course of investigation under this order shall be CPDL’s exclusive property and shall not be used for any other purpose except for the execution of the order.

The technical information drawing, records and other document shall not be copied in any form, transferred, or divulged and/or disclosed to third party in full/part, not misused in any form whatsoever except to the extent for the execution of the order. The technical information, drawing and other related documents shall be returned to CPDL with all approved copies and duplicates including drawing/plans as are prepared by the Supplier during the executions of this order, if any, immediately after they have been used for agreed purpose.

In the event of any breach of this provision, the contractor shall indemnify CPDL against any loss, cost or damage or claim by any party in respect of such breach.

Both parties undertake to keep confidential all information (written as well as oral) concerning the business, processes and affairs of the other, which has been obtained or received as a result of the selection process, discussions leading up to, or the entering/execution of the Contract.

CPDL shall not use such documents, data, and other information received from the Selected Bidder for any purposes unrelated to the Contract.  Similarly, the Bidder shall not use such documents, data, and other information received from CPDL for any purpose other than the services required for the performance of the Contract.

Each of the parties to this contract undertakes to the other to take all such steps as shall from time to time be necessary to ensure compliance with the provisions of the above clauses by its employees, agents and subcontractors.

In continuation with the above provisions, each Bidder shall enter into a Mutual Non- Disclosure Agreement with CPDL, which will form an essential part of the entire selection process. The same has been provided as Annexure-7

##### RECOVERIES

Whenever under this Purchase Order any money is recoverable from and payable by the Supplier, CPDL shall be entitled to recover such sum by appropriating in part or in whole by detecting any sum due to which any time thereafter may become due from the Supplier in this or any other contract. Should the sum be not sufficient to cover the full amount recoverable the Supplier shall pay to the CPDL on demand the remaining balance.

##### COMPLIANCE WITH APPLICABLE LAWS

Supplier warrants that all Supplies purchased under the Purchase Order shall conform to all applicable Cities, State and Central laws, ordinances and all relevant statutory regulations. Further, Supplier shall defend and save CPDL harmless from loss, cost or damage by reason of any actual or alleged violation thereof.

##### GOVERNING LAW AND JURISDICTION OF CONTRACT

The Purchase Order shall be governed, construed and interpreted in accordance with the laws of India. The court at Chandigarh shall have the exclusive jurisdiction in respect of all matters pertaining to this Tender Notification.

##### INDEMNIFICATION

Notwithstanding contrary to anything contained in this RFQ, Supplier shall at his costs and risks make good any loss or damage to the property of the CPDL and/or the other Supplier engaged by the CPDL and/or the employees of the CPDL and/or employees of the other Supplier engaged by the CPDL whatsoever arising out of the negligence of the Supplier while performing the obligations under this contract.

##### TERMINATION FOR CONVENIENCE OF PURCHASER

CPDL at its sole discretion may terminate the contract by giving 30 days prior notice in writing or through email to the Supplier. CPDL shall pay the Supplier for all the supplies/ services rendered till the actual date of Purchase Order termination against submission of invoice by the Supplier to that effect.

Payment of such compensation is the sole and exclusive remedy of the supplier for termination of this Agreement by CPDL hereunder and the supplier shall not be entitled to, and hereby waives, claims for lost profits and all other damages and expenses, directly or indirectly caused by the termination.

Supplier hereby agrees that substantiation for settlement of any claims submitted by supplier shall be complete and in sufficient detail to allow CPDL’s evaluation. Terminate all sub contracts except those have been/ to be assigned to the CPDL all rights, titles and benefits of the Suppliers/Vendor as the case may be.

##### PURCHASE ORDER ACCEPTANCE

The Supplier shall within 07 (seven) days from the date of the receipt of the Purchase Order confirm their acknowledgement/unconditional acceptance in its entirety without any deviations by returning two copies of the Purchase Order duly signed by the Supplier’s power of attorney holder having the authority to sign and accept such Purchase Order on each page as a token of their acceptance to the designated persons mentioned in the Purchase Order. Signature on every page shall be with Supplier’s company’s seal.

In the event, the Supplier fails to submit the Order acknowledgment/acceptance within the above specified period, CPDL reserves the right to cancel the Purchase Order without prejudice to other rights and remedies which CPDL may be entitled to, as per terms and conditions of the Purchase Order.

With Supplier's acceptance of the Purchase Order, Supplier is deemed to have waived all general sales conditions enclosed with their offer and same shall be deemed to have been withdrawn unconditionally.

If any of the provisions of Supplier’s proposal and subsequent correspondence is in conflict with the terms and conditions of the Purchase Order, the latter shall govern.

Annexure-1: Sustainable Procurement Policy

In journey of achieving sustainability objectives, This Policy outlines CPDL expectations from its suppliers/contractors on key parameters i.e. Environment, Ethics, Society & Quality. This policy and its implementation will also encourage our suppliers to adopt practices that minimise environmental impact, maintain quality and ethical standards and results positive social impact.

CPDL as a responsible & environment conscious organization has always considered importance to environment, Business ethics, society and quality as a measure for sustainability. CPDL also expects from its suppliers to contribute to our sustainability objectives. We understand our suppliers are different in terms of scale of their operations, geography they operate. Considering the same, general objectives are mentioned below for all type of suppliers to follow and participate in our journey of sustainable sourcing as per their capacity.

The Sustainable Procurement Policy of CPDL is based on the following parameters:

1. Environment:

Our suppliers should recognize their environmental responsibility in identifying the environmental impact of their manufacturing activities and minimize the adverse effects on the community in the following manners: -

a) Suppliers must understand the environmental impacts of their products and services throughout their entire lifecycle and consider to apply circular economy principles.

b) Suppliers must take efforts to continually improve the environmental performance by setting objectives, targets, and processes for efficient use of natural resources, energy, water.

c) Suppliers must prevent on use of ROHS (Restriction of Hazardous Substance) or toxic substances.

d) Suppliers must focus on waste minimization, emission reduction, and pollution prevention and submit action plan on annual basis or as & when required by CPDL.

e) Supplier should ensure to adopt LCA (Life Cycle Assessment) methodology of their product time to time and to work on action plan of improvement to reduce Environmental Impact.

f) Supplier must be compliant to local environment laws and submit proof on periodic basis, as & when required by CPDL.

g) Suppliers must make necessary arrangements for disposing waste/toxic materials through authorized waste processors only and to follow state pollution guidelines for storage and disposal of items and submit copy of proof on periodic basis.

h) Suppliers should ensure and promote eco-friendly manufacturing process with minimum and environmentally compatible/recyclable packaging.

i) Supplier should innovate cost effective energy efficient green products.

j) Suppliers should try to minimize use of all resources through innovation. Supplier should try to take steps to reduce environmental impact of all packaging material by developing innovative, practical solution.

k) Supplier should ensure & promote to opt for "EDP (Environment declared product)" & "Green product certification" & should opt for following certifications: -

- ISO 50001 (Energy Management System)

- ISO 14001 (Environment Management System)

2.  Society: -

We require our suppliers to adopt practices that maximize positive social impacts, enabling equality, equity, inclusion, and Local community development.

a) Supplier must comply with applicable legal & statutory requirements related to health & safety.

b) Supplier must not indulge child labour below 18 years for work in their unit.

c) Supplier must comply with minimum wages & workman compensation act.

d) Supplier should opt for following certifications: -

- ISO 45001 (Occupational Health and Safety Management System)

3.  Business Ethics: -

We expect our suppliers to conduct all business activities in a fair & transparent way with ensuring integrity & ethics.

a)  Suppliers must comply with fair competition and anti-corruption regulations; avoid conflicts of interest.

b)  Suppliers must spread awareness on sustainable procurement with their business associates & channel partners.

c) Supplier must properly manage and protect confidential information related to our business activities in compliance with domestic and international laws and regulations as well as our internal rules and policies.

d) Suppliers must conduct business activities with high ethical and moral standards and respect Human Rights considerations of other stakeholders, including their employees.

e) Supplier should opt for following certifications: -

- ISO 27001 (Information Security Management System)

4.  Quality: -

Supplier must ensure sufficient product design safety and sell products with an awareness of its responsibility as a manufacturer. Product safety must be ensured in compliance with laws and regulations.

a)  Suppliers must establish and promote a quality management system that develops an organizational structure, outlines an activity plan, and specifies responsibility assignment and procedures

b)  Suppliers must integrate eco-design principles in product development; efficient machines and good manufacturing practices.

c) Supplier must procure with certification and eco-labels wherever applicable.

d) Supplier should opt for following certifications: -

- ISO 9001 (Quality Management System)

Implementation of Policy

CPDL is committed to deliver sustainable outcomes through various sourcing process adopted, procurement activities & processes. We expect our suppliers to design their policy including monitoring and improvement mechanism.

CPDL shall also consider to work jointly with suppliers for innovative environment friendly products, waste reduction, sharing of best practices etc. Such collaborative approach of sustainability shall help in achieving various sustainable goals.

We expect our suppliers to monitor and report various initiatives undertaken by them with regard to adherence of this policy & CPDL may inspect the manufacturing facility or factory of the other party to ascertain standards, quality control measures, or specific requirements.

For further information or any query related to this policy, suppliers can contact to: -

Mr. Narinder Pal Singh (C&MM) through email id narinderpal.singh@rpsg.in

ANNEXURE 2:

ACCEPTANCE FORM FOR PARTICIPATION IN REVERSE AUCTION EVENT

(To be signed & stamped by the bidder along-with bid)

Chandigarh Power Distribution Limited (CPDL) may conduct reverse auction through online tool as an integral part of entire tendering process. All techno-commercially qualified bidders shall participate in the reverse auction.

The following terms and conditions are deemed as accepted by the bidder on participation in the bid:

- In case of bidding through Internet medium, bidders are advised to ensure availability of all associated infrastructure as required to participate in the reverse auction event. Inability to bid due to telephone glitch, internet response issues, software & hardware hangs/failures, power failures or any other reason shall not be the responsibility of CPDL.

- In case bidder fails to participate in the reverse auction event due to any reason whatsoever, it shall be presumed that the bidder has no further discounts to offer and the initial bid submitted by them as a part of tender shall be considered as bidder’s Final No Regret offer. Any off-line price bids received from a bidder in lieu of non-participation in the reverse auction event shall be rejected by CPDL.

- The bidder is advised to understand the auto bid process to safeguard themselves against any possibility of nonparticipation in the reverse auction event.

- The bidder shall be prepared with competitive price quotes during the day of reverse auction event.

- The prices quoted by bidder in reverse auction event shall be on FOR Landed cost CPDL Store/site basis inclusive of all relevant taxes, duties, levies, transportation charges etc on line item wise or on total lumpsum basis, this shall be communicated to bidders before conducting RA.

- The prices submitted by the bidder during reverse auction event shall be binding on the Bidder.

- The bidder agrees to non-disclosure of trade information regarding bid details e.g. purchase, Identity, bid process/technology, bid documentation etc.

- CPDL will make every effort to make the bid process transparent. However, award decision of CPDL will be final and binding on the bidder.

- The prices submitted during reverse auction event shall be binding on the bidder.

- No request for Time extension of the reverse auction event shall be considered by CPDL.

- CPDL shall provide the user id and password to the authorized representative of the bidder. Authorization letter in lieu of the same shall be submitted along with the signed and stamped acceptance form.

- The original price bids of the bidders shall be reduced on pro-rata basis against each line item based on the final all-inclusive prices offered during conclusion of the reverse auction event for arriving at contract amount.

##### ANNEXURE-3

##### MANUFACTURER AUTHORIZATION FORM

(To be submitted on OEM’s Letter Head)

Date:-

Tender No.:

To

Deputy Manager (C&MM)

Chandigarh Power Distribution Limited

SCO 33-35, 4th Floor, Sector 34-A

Chandigarh - 160022, India

Sir,

WHEREAS M/s. [name of OEM], who are official manufacturers of _______________________	having factories at [address of OEM] do hereby authorize M/s [name of bidder] to submit a Bid in relation to the Invitation for Bids indicated above, the purpose of which is to provide the following Goods, manufactured by us

……………………………………………………………………………………………………and to subsequently negotiate and sign the Contract.

We hereby extend our full guarantee and warranty in accordance with the Conditions of Contract or as mentioned elsewhere in the Tender Document, with respect to the Goods offered by the above firm in reply to this Invitation for Bids.

We hereby confirm that in case, the channel partner fails to provide the necessary services as per the Tender Document referred above, M/s [name of OEM] shall provide standard warranty on the materials supplied against the contract. The warranty period and inclusion / exclusion of parts in the warranty shall remain same as defined in the contract issued to our channel partner against this tender.

Yours Sincerely,

For ……………..

Authorized Signatory

##### ANNEXURE-4:

##### DEVIATIONS SHEET

Vendor shall refrain from taking any deviations on this TENDER. Still, in case of any deviations, all such deviations from this tender shall be set out by the Bidder, Clause by Clause in this schedule and submit the same as a part of the Technical Bid.

Unless specifically mentioned in this schedule, the tender shall be deemed to confirm the CPDL’s specifications:

Technical Deviations: -

| SL No. | Clause No. | Page No. | Clause Descriptions | Details of Clarification/deviation with justifications |
| --- | --- | --- | --- | --- |

Commercial Deviations: -

| SL No. | Clause No. | Page No. | Clause Descriptions | Details of Clarification/deviation with justifications |
| --- | --- | --- | --- | --- |

By signing this document, we hereby withdraw all the deviations whatsoever taken anywhere in this bid document and comply with all the terms and conditions, technical specifications, scope of work etc. as mentioned in the standard document except those mentioned above.

Seal of the Bidder:

Signature:

Name:

ANNEXURE-5

FORMAT OF CONTRACT PERFORMANCE BANK GUARANTEE

[Stamp paper]

PERFORMANCE BANK GUARANTEE

M/s. Chandigarh Power Distribution Limited

CPDL, 4th Floor, SCO 33 to 35,

Sector 34A, Chandigarh, 160022

Whereas Chandigarh Power Distribution Limited. (hereinafter referred to as the “Purchaser”, which expression shall unless repugnant to the context or meaning thereof include its successors, administrators and assigns) has awarded to M/s ________, (Name of Vendor) ____________________(Address of Vendor) (hereinafter referred to as the “Supplier” which expression shall unless repugnant to the context or meaning thereof include its successors, administrators, executors and assigns), a Purchase/Work Order(whichever is applicable) No. __________ dt. ________ for supply/implementation(whichever is applicable) of ____________________________ (the Contract).

And whereas the value of the Contract is Rs. _______ (Rupees______________________Only).

(the contract value).

And whereas it is a condition of the contract that the supplier shall provide a Performance Bank Guarantee for the due and faithful performance of the entire Contract for a sum equivalent to 10% of the Contract Value i.e. Rs. ____________/-(Amount of Bank Guarantee) (Rupees _______________________ Only) to the Purchaser on or before _______

(Date of validity).

And whereas the Bank under instructions from the Supplier has agreed to guarantee the due performance of the Contract.

Now it is agreed as follows :

- We, __________(Name of issuing Bank), _______________________(Address of Issuing Branch) having its Head Office at ________(Address of Head office) (hereinafter referred to as the Bank, which expression shall unless repugnant to the context or meaning thereof, include its successors, administrators, executors and assigns) shall indemnify and keep indemnified the Purchaser for, and guarantee and undertake to pay to the Purchaser immediately on demand, a sum equivalent to 10% i.e. Rs. _____________/-(Amount of Bank Guarantee) (Rupees __________________________ Only) of the contract value as aforesaid at any time upto _____________(Last Date of validity) without any demur, reservation, contest, recourse or protest and/or without any reference to the Supplier, against all losses, damages, costs and expenses that may be caused to or suffered by the Purchaser by reason of any default on the part of the Supplier in performing and observing any and all the terms and conditions of the Contract or breach on the part of the Supplier of terms or conditions of the Contract.

- The demand shall consist only of an original letter issued by Purchaser stating that the Supplier has failed to fulfill its obligations under the Contract.  Such demand made by the Purchaser on the Bank shall be conclusive and binding notwithstanding any difference or dispute between the Purchaser and the Supplier or any difference or dispute pending before any Court, Tribunal, Arbitrator or any other authority.

- The Bank Guarantee undertakes not to revoke this guarantee during its currency without previous written consent of the Purchaser and further agrees that the guarantee herein contained shall continue to be enforceable during the period that would be taken for satisfactory performance and fulfillment in all respects of the contract or in the event of any dispute between the Purchaser and Supplier until the dispute is settled (provided that the claim/demand under this guarantee is lodged/referred during the currency of this guarantee) or till the Purchaser discharges this guarantee whichever is earlier.

- The Purchaser shall have the fullest liberty without affecting in any way the liability of the Bank under this guarantee from time to time to extend the time for performance of the Contract by the Supplier.  The Purchaser shall have the fullest liberty, without affecting the liability of the Bank under this guarantee, to postpone from time to time the exercise of any powers vested in them or of any right which they might have against the Supplier, and to exercise the same at any time in any manner, and either to any other course or remedy or security available to the Purchaser. The bank shall not be released of its obligations under these presents by any exercise of the Purchaser of its liberty with reference to the matters aforesaid or any of them or by reason of any other act or forbearance or other acts of omission or commission on the part the Purchaser or any other indulgence shown by the Purchaser of by any other matter or thing whatsoever which under law would, but for this provision, have the effect of relieving the Bank.

- The Bank agrees that the Purchaser at its option shall be entitled to enforce this guarantee against the Bank as a principal debtor, in the first instance without proceeding against the Supplier and notwithstanding any security or other guarantee that the Purchaser may have in relation to the Supplier’s liabilities.

- Any payment made hereunder shall be made free and clear of, and without deduction for or on account of any present or future taxes, levies, imposts, duties, charges, fees, deductions, or withholdings of any nature whatsoever and whomsoever imposed. We unconditionally acknowledge that any such demand by purchaser of the amount payable by us up to the aggregate maximum amount of this guarantee as mentioned above, to the purchaser during this guarantee’s validity shall be final, binding and conclusive evidence in respect of amount payable by the supplier to the purchaser.

- Confirmation of this Bank guarantee may be obtained by the beneficiary from the following :-

Name 			-

Designation		-    Most Important if not  mentioned reject the BG

Contact No.		-

Email ID		-

- This Performance Bank Guarantee shall be governed by the laws of India.

NOTWITHSTANDING anything contained in herein above:

- Our liability under this Bank Guarantee is restricted to a maximum of Rs. _________/- (Amount of Bank Guarantee) (Rupees ________)

- This Bank Guarantee shall be valid upto ________(Last Date of validity).

- We are liable to pay the guaranteed amount or any part thereof under this Bank Guarantee only and only if you serve upon us a written claim or demand on or before ____________(Last Date of claim).

Dated this………..day of ……………2016 at ……………………….

Witness

1.

2.

ANNEXURE-6:

FORMAT OF WARRANTY/GUARANTEE CERTIFICATE

Ref. Purchase Order No.:

Dear Sir,

We hereby confirm that the (item name) dispatched vide invoice no. ____ dated ____ is warranted / guaranteed against defective material & faulty workmanship, for a period of ____ months from date of installation / commissioning and ____ months from date of delivery, whichever is earlier.

If the supplied equipment found defective under normal operating condition during this period it will be replaced or repaired free of charge if returned to us.

For __________________________

AUTHORISED SIGNATORY

Date :

Company Seal :

Vendors Name & Signature

ANNEXURE -7

Mutual Non-Disclosure Agreement

This Non-Disclosure Agreement is between Chandigarh Power Distribution Limited (CPDL) having its principal place of business at SCO 33-35, 4th Floor, Sector 34-A Chandigarh - 160022, India and __________(Name of the Party)_____________________________ (Company) having its principal place of business at __________(Address)____________________________________ and is effective as of _____________(date)_______________.

CPDL and Company are hereinafter jointly referred to as the “Parties” or individually as “Party”.

- Confidential Information

Confidential Information is any information that is disclosed by one party and/or its affiliates (“Discloser”) to the other party and/or its affiliates (“Recipient”) and is either:

- conspicuously marked as confidential, proprietary or the like;

- clearly identified as confidential, proprietary or the like at the time of oral disclosure, and confirmed as confidential, proprietary or the like in writing within 14 days by Discloser; or

- information concerning Discloser's products or services, plans or roadmaps, current or future business, network architecture and systems, financial information, and such other information disclosed for the purpose of evaluating a potential business relationship between the parties, that Recipient knows or reasonably ought to know, is Discloser's confidential information.

- information which has been conveyed by either party as the confidential information.

However, Confidential Information excludes any information that is:

- publicly available without breach of this agreement by Recipient;

- known by Recipient without confidentiality obligations; or

- independently developed by or for Recipient for its own use.

- Disclosure of Confidential Information

Recipient may disclose Discloser's Confidential Information only on a need-to-know basis and only to its Employees, to other companies engaged by Recipient to perform services, and to individuals working for Recipient or for these other companies.  However, each of these other companies and individuals who receives Discloser's Confidential Information must have written confidentiality obligations in place with Recipient that protect Discloser's Confidential Information at least as much as this agreement.  Recipient may also disclose Discloser's Confidential Information when required by a court or government order if Discloser is given written notice prior to the disclosure and an opportunity to oppose such disclosure.

- Protection

Recipient must protect Discloser's Confidential Information to the same degree and standard of care that Recipient protects its own confidential information of like nature.

- Use

Recipient may use Discloser's Confidential Information only:

- to evaluate opportunities to do business with Discloser;

- for the purpose that Discloser conspicuously marked upon its Confidential Information, if any; or

- in accordance with a written, signed agreement, if any, between Recipient and Discloser that includes an express license or permission to use specific Confidential Information of Discloser.

- Return or destruction

Recipient must, within 30 days, comply with Discloser's written requests, made to Recipient's legal, compliance, or like department, to return or destroy specific Confidential Information of Discloser.

Within seven (7) days of a written request by the Disclosing Party, the Receiving Party shall return/destroy (as may be requested in writing by the Disclosing Party or upon expiry and or earlier termination) all originals, copies, reproductions and summaries of Confidential Information provided to the Receiving Party as Confidential Information.  The Receiving Party shall certify to the Disclosing Party in writing that it has satisfied its obligations under this paragraph.

- Termination

The obligations and restrictions in Sections 2 (Disclosure of Confidential Information), 3 (Protection), 4 (Use) and 5 (Return or destruction) terminate, with respect to specific disclosures of Confidential Information, 5 years after the date Discloser first made such disclosure to Recipient.  Either party may terminate the rest of this agreement by written notice to the other party's legal, compliance or like department. However, Section 7 (Retained rights) survives any termination.

- Retained rights

Discloser retains all rights to its Confidential Information. This agreement does not grant any express or implied license to any trademark, copyright, patent or similar right other than the limited right to make exact copies upon disclosure in accordance with section 2 (Disclosure of Confidential Information). Confidential Information is disclosed "AS IS" under this agreement.  Discloser is not liable under this agreement for the accuracy or completeness of its Confidential Information. There are no express or implied representations or warranties by Discloser or Recipient under this agreement, including those with respect to the infringement of any intellectual property, privacy or third-party rights.

- Limitations

This agreement does not:

- prohibit Recipient from independently developing products, services, solutions and technologies similar to, or competitive with, those contemplated by Discloser's Confidential Information;

- require Recipient to limit its work assignments;

- give Recipient or Discloser assurances of future revenue, profit or business; or

- create relationships of partnership, agency or the like.

- Miscellaneous

The laws of the Republic of India govern all matters arising out of or related to this agreement.  No party may assign any rights under this agreement.  Each party acknowledges that monetary remedies may be inadequate to protect Confidential Information and that Discloser may seek injunctive relief in the event of any threatened or actual breach of this agreement without prejudice to other remedies available in equity and in law. This agreement is the entire agreement on the matters contemplated by this agreement, and all negotiations, discussions and agreements on these matters are expressly merged into, and superseded by, this agreement.  Failure to enforce any part of this agreement is not a waiver.  This agreement may be modified or amended by only a written agreement by the parties.  The parties must comply with all laws and regulations that apply to their disclosure and receipt of Confidential Information, including those applicable to export and import.  The parties may assent to this agreement electronically or sign this agreement manually and may do so in counterparts.  Each individual electronically assenting to or manually signing is authorized to do so on behalf of his or her respective party and bind the party to this agreement.

The parties are signing this Mutual Non-Disclosure Agreement.

| Agreed by: | Agreed by: |
| --- | --- |
| ______________________ (“CPDL”) | _________________“Company”) |
| By _____________________________________ Authorized Signature | By __________________________________ Authorized Signature |
| Name: | Name: |
| Date: | Date: |

SECTION – V: PRICE BID FORMAT

| Sl. No |  | Item Description | UOM | Qty | Basic Rate (Rs.) | Freight (Rs.) | GST (Rs.) | Unit Landed Rate (Rs.) | Total Landed Price (Rs.) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Q | A | B | C = (A+B)*18% | D = A+B+C | E= Q X D |
| 1 | HT Cable | 11kV 3C X 300 Sq mm | Mtr | 1,11,000 |  |  |  |  |  |
| 2 |  | 11kV 3C X 70 Sq mm | Mtr | 3,000 |  |  |  |  |  |
| 3 | LT Cable | 1.1 kV 4C X 400 Sq mm | Mtr | 27,000 |  |  |  |  |  |
| 4 |  | 1.1 kV 4C X 150 Sq mm | Mtr | 8,000 |  |  |  |  |  |
| 5 |  | 1.1 kV 4C X 95 Sq mm | Mtr | 1,98,000 |  |  |  |  |  |
| 6 |  | 1.1 kV 4C X 50 Sq mm | Mtr | 60,000 |  |  |  |  |  |
| 7 |  | 1.1 kV 4C X 35 Sq mm | Mtr | 60,000 |  |  |  |  |  |
| 8 |  | 1.1 kV 4C X 16 Sq mm | Mtr | 1,00,000 |  |  |  |  |  |
| 9 |  | 1.1 kV 2C X 10 Sq mm | Mtr | 1,00,000 |  |  |  |  |  |

NOTE:

- The prices mentioned above shall be on an F.O.R basis at CPDL Store/Site.

- The prices shall be variable as per Latest IEEMA Price Variation formula.

- The bidders are advised to quote prices strictly in the above format. Failing to do so, bids shall be liable for rejection.

- The bidder must fill every column of the above format. Mentioning “extra/inclusive”/other conditions in any of the column may lead to rejection of the price bid.

- No cutting/ overwriting in the prices is permissible.

- The quantity mentioned above is for evaluation purposes only and may vary as per actual site requirement.

We declare that the following are our quoted prices in INR for the entire project/schemes.

Date:

Bidder Name:

Place: Bidders Address:

Name & Signature …………………………………………………….

Designation: ………………………………………………………………

Common Seal: …………………………………………………………….

SECTION-VI

GENERAL FORMATS (APPENDIX)

Appendix- I

COMMERCIAL TERMS AND CONDITIONS – SUPPLY

| SR. NO. | ITEM DESCRIPTION | AS PER CPDL | BIDDER’S CONFIRMATION |
| --- | --- | --- | --- |
| 1 | VALIDITY |  |  |
| 2 | PRICE BASIS |  |  |
| 3 | PAYMENT TERMS |  |  |
| 4 | COMPLETION TIME |  |  |
| 5 | DEFECT LIABILITY PERIOD |  |  |
| 6 | LIQUIDATED DAMAGES |  |  |
| 7 | CONTRACT PERFORMANCE BANK GUARANTEE |  |  |

APPENDIX II

BID FORM

Deputy Manager

Purchase Department,

Chandigarh Power Distribution Limited

SCO 33-35, 4th Floor, Sector 34-A

Chandigarh - 160022, India

Sir,

1. We understand that CPDL is desirous of execution of

………………………………………………………………………………………………… (Name of work).

2.  Having examined the Bidding Documents for the above-named works, we the undersigned, offer to deliver the goods in full conformity with the Terms and Conditions and technical specifications for the sum indicated in Price Bid or such other sums as may be determined in accordance with the terms and conditions of the contract. The above amounts are in accordance with the Price Schedules attached herewith and are made part of this bid.

3. If our Bid is accepted, we undertake to deliver the entire goods as) as per delivery schedule mentioned in Section IV from the date of award of purchase order/letter of intent.

4. If our Bid is accepted, we will furnish a Contract performance bank guarantee as per Bid document for due performance of the Contract in accordance with the Terms and Conditions.

5. We agree to abide by this Bid for a period of 120 days from the due date of bid submission & subsequent corrigendum/amendment/extension of due date of submission. It shall remain binding upon us and may be accepted at any time before the expiration of that period.

6. We declare that we have studied the provision of Indian Laws for supply of equipment / materials and the prices have been quoted accordingly.

7. Unless and until Letter of Intent is issued, this Bid, together with your written acceptance thereof, shall constitute a binding contract between us.

8. We understand that you are not bound to accept the lowest, or any bid you may receive.

9. There is provision for Resolution of Disputes under this Contract, in accordance with the Laws and Jurisdiction of Contract.

Dated this............................... day of................................................. 20….

Signature................................ In the capacity of ………………………………. duly authorized to sign for and on behalf of (IN BLOCK CAPITALS) ..................................................................

APPENDIX III

FORMAT FOR EMD BANK GUARANTEE

(To be issued in a Non-Judicial Stamp Paper of Rs.50/-purchased in the name of the bank)

Whereas [name of the Bidder] (herein after called the “Bidder”) has submitted its bid dated [date of submission of bid] for the supply of [name and/or description of the goods] (here after called the “Bid”).

KNOW ALL PEOPLE by these presents that WE [name of bank] at [Branch Name and address], having our registered office at [address of the registered office of the bank] (herein after called the “Bank”), are bound unto Chandigarh Power Distribution Limited, with its Corporate Office at SCO 33-35, 4th Floor, Sector 34-A Chandigarh - 160022, India, (herein after called —the “Purchaser”) in the sum of Rs. ……………/- (Rupees ……………………………….. only) for which payment well and truly to be made to the said Purchaser, the Bank binds itself, its successors, and assigns by these presents.

Sealed with the Common Seal of the said Bank this_____ day of________ 20____.

THE CONDITIONS of this obligation are:

1 If the Bidder withdraws its Bid during the period of bid validity specified by the Bidder on the Bid Form; or

2. If the Bidder, having been notified of the acceptance of its Bid by the Purchaser during the period of bid validity:

(a) Fails or refuses to execute the Contract Form, if required; or

(b) Fails or refuses to furnish the performance security, In accordance with the

Instructions to Bidders/ Terms and Conditions;

We undertake to pay to the Purchaser up to the above amount upon receipt of its first written demand, without the Purchaser having to substantiate its demand, provided that is its demand the purchaser will note that amount claimed by it is due to it, owing to the occurrence of one or both of the two condition(s), specifying the occurred condition or condition(s).

This guarantee will remain in force up to and including One Hundred Twenty (120) days after the due date of submission bid, and any demand in respect thereof should reach the Bank not later than the above date.

(Stamp & Signature of the bank)

Signature of the witness

APPENDIX – IV

LITIGATION HISTORY

| Year | Name of client | Details of contract & date | Cause of Litigation / arbitration | Disputed Amount |
| --- | --- | --- | --- | --- |

APPENDIX – V

CURRENT CONTRACT COMMITMENTS/ WORK IN PROGRESS

| Year | Name of client | Details of contract & date | Value of Outstanding Work | Estimated Completion Date |
| --- | --- | --- | --- | --- |

APPENDIX – VI

FINANCIAL DATA

(Duly Certified by Chartered Accountant)

|  | FY 21-22 | FY 22-23 | FY 23-24 | FY 24-25 |
| --- | --- | --- | --- | --- |
| Total assets |  |  |  |  |
| Current assets |  |  |  |  |
| Total Liability |  |  |  |  |
| Current Liability |  |  |  |  |
| Profit before taxes |  |  |  |  |
| Profit after taxes |  |  |  |  |
| Sales Turnover |  |  |  |  |

APPENDIX VII

CHECK LIST

| Sr. No. | Description | Compliance |
| --- | --- | --- |
| 1 | Index | Yes/No |
| 2 | Covering Letter | Yes/No |
| 3 | Bid Form Duly Signed | Yes/No |
| 4 | Documents in Support of Qualification Criteria | Yes/No |
| 5 | Technical Bid | Yes/No |
| 6 | Acceptance to Commercial Terms and Conditions | Yes/No |
| 7 | Financial Bid (in password Protected File) | Yes/No |
| 8 | EMD | Yes/No |
| 9 | Tender Fee | Yes/No |
| 10 | Power of Attorney/Authorisation Letter for Signing the Bid | Yes/No |
| 11 | Financial Data in Tabular Format | Yes/No |
| 12 | List of Current Commitments/ Work in Progress | Yes/No |
| 13 | Bank Solvency Certificate | Yes/No |
| 14 | No Litigation Certificate | Yes/No |

APPENDIX VIII

TECHNICAL BID SUBMISSION CHECKLIST

##### Submission of this duly filled checklist along with the bid is mandatory. The Order of Documents shall be as follows:

Bids with incomplete/ wrong information are liable for rejection.

| S. No. | Description | CPDL Requirement | Bidder's Compliance (Yes/No/ Not Applicable) |
| --- | --- | --- | --- |
| 1 | Tender No. | Required |  |
| 2 | Tender Fee, EMD & Signed Bid Form as mentioned in the tender, if applicable | Required |  |
| 3 | Bidder Details |  |  |
| 3.1 | Name of the Bidder | Required |  |
| 3.2 | Company Profile/Organogram | Required |  |
| 3.3 | Name of duly Authorized contact person (along with Authorizations to submit the Bid) | Required |  |
| 3.4 | Contact No. of duly Authorized contact person | Required |  |
| 3.5 | E-mail Id of duly Authorized contact person | Required |  |
| 4 | Documents Submission Format |  |  |
| 4.1 | Documents shall be submitted in Scan copy of Original pdf for online mode. Any other format is not acceptable | Required |  |
| 4.2 | Index of documents with page numbers for each document | Required |  |
| 5 | Signed Copy of tender as an unconditional acceptance | Required |  |
| 6 | Qualification Criteria Requirement Compliance, If applicable |  |  |
| 6.1 | Summary of compliance of qualifying criteria in tabular form along with details of documentary proof provided | Required |  |
| 6.2 | Detailed Documents supporting compliance of qualifying criteria | Required |  |
| 7 | Technical Specification reference number | Required |  |
| 8 | Drawings/ Documents as per Technical Specification |  |  |
| 8.1 | Signed copy of technical specification | Required |  |
| 8.2 | Type Test reports of offered model/ type/ rating | Required |  |
| 8.3 | Guaranteed Technical particulars (GTP) | Required |  |
| 8.4 | Deviation Sheet – Technical (along with soft editable copy) | Required |  |
| 8.5 | Detailed Drawings | Required |  |
| 8.6 | Manufacturer's quality assurance plan | Required |  |
| 8.7 | Other drawings/ documents mentioned in technical specification | Required |  |
| 9 | Deviation Sheet – commercial (along with soft editable copy) | Required |  |
| 10 | Samples as per technical specification if applicable | Required |  |

SECTION-VII

TECHNICAL SPECIFICATION

Drafting Note: On Non Judicial Stamp Paper of Appropriate Value as per Stamp Act relevant to the place of execution